# Inverter module

Macro file name: SSIM.mac

Macro name: SSIM, NLAM_SSIM

Version number: NCS 3.1

The inverter module is a DC/AC converter that provides clean 3-phase AC power to a variety of loads. . Figure 1 depicts the power converter topology used to implement the inverter module. As shown, this component consists of an input capacitor, a 3-phase fully controlled bridge converter, an output LC filter, and the control algorithms. The LC filter, illustrated in Figure 2, is used to filter the switching frequency component harmonics from the output in order to provide clean ac power to its loads.

The overall control of the inverter module contains a voltage control loop and a synchronous current regulator (SCR).  A diagram of the voltage control loop is shown in Figure 3.  The voltage control loop drives the error in the output voltage to zero by generating a current command through the use of a PI regulator with decoupling and feed-forward control.  The voltage control loop takes as inputs the desired output voltage and the desired output frequency.  A synchronous current regulator shown in Figure 4, uses the current command from the voltage control loop and actively regulates the fundamental component of the current so the command is exactly achieved.  A hysteretic/delta modulator regulates the current in the output filter inductors to the SCR commanded value.  It generates the switching commands for the power semiconductors.

Fig 1.  Inverter module

Figure 2. Inverter module filter

Figure 3. Inverter control

Figure 4  Synchronous current regulator.

SSIM : Detailed Model

Author: S. D. Sudhoff

Author contact: sudhoff@purdue.edu,

Date:

Macro name: SSIM

Version number:  NCS 3.1

Report errors or changes to: sudhoff@purdue.edu

# Brief Description

# Detailed model of a ship service inverter module.

# List of Inputs, Outputs, Parameters, and Internal variable

| Variable Name | Description | Units |
| --- | --- | --- |
| z | Concatenation variable |  |

| Input Variable Name | Description | Units |
| --- | --- | --- |
| on | Logical command to turn on converter | logical |
| off | Logical command to turn off converter | logical |
| vdc | Inverter module DC input voltage | V |
| iaO | a-phase current out of the inverter module | A |
| ibO | b-phase current out of the inverter module | A |

| Output Variable Name | Description | Units |
| --- | --- | --- |
| vthev | Instantaneous Thevinen equivalent input voltage | V |
| rthev | Instantaneous Thevinen equivalent input resistance |  |
| vabO | a- to b-phase output voltage | V |
| vbcO | b- to c-phase output voltage | V |
| vcaO | c- to a-phase output voltage | V |

| Parameter Name | Description | Default Value | Units |
| --- | --- | --- | --- |
| Set Up |  |  |  |
| vqe∗ | q-axis voltage command |  | V |
| ωe | Command output frequency |  | rad/s |
| Bridge |  |  |  |
| Cin | Input capacitance |  | F |
| rCin | Input capacitor effective series resistance |  |  |
| vsw | Switch nominal forward voltage drop |  | V |
| rsw | Switch forward resistance |  |  |
| vd | diode nominal forward voltage drop |  | V |
| rd | diode forward resistance |  |  |
| LC Filter |  |  |  |
| Lac | Inductance of AC filter |  | H |
| rL | Series resistance of inductor |  |  |
| Cac | Capacitor in delta-connection |  | F |
| rC | Series resistance of capacitor |  |  |
| Supervisory Control |  |  |  |
| vinmin1 | Lowest input voltage to start converter |  | V |
| vinmax1 | Highest input voltage to start converter |  | V |
| vinmin2 | Lowest input voltage to keep running |  | V |
| vinmax2 | Highest input voltage to keep running |  | V |
| τsc | Time constant of supervisory control |  | second |
| Sensors |  |  |  |
| gainVab | gain of a- to b-phase output voltage sensor |  |  |
| offsetVab | offset of a- to b-phase output voltage sensor |  | V |
| gainVbc | gain of b- to c-phase output voltage sensor |  |  |
| offsetVbc | offset of b- to c-phase output voltage sensor |  | V |
| gainiaO | gain of a -phase output current sensor |  |  |
| offsetiaO | offset of a- to b-phase output current sensor |  | A |
| gainibO | gain of b-phase output current sensor |  |  |
| offsetibO | offset of b-phase output current sensor |  | A |
| gainiaL | gain of a-phase inductor current sensor |  |  |
| offsetiaL | offset of a-phase inductor current sensor |  | A |
| gainibL | gain of b-phase inductor current sensor |  |  |
| offsetibL | offset of b-phase inductor current sensor |  | A |
| Voltage Control |  |  |  |
| Kpv | Voltage control proportional gain |  | A/V |
| Kiv | Voltage control integral gain |  | A/Vs |
| Ceq | estimated equivalent line-neutral capacitance |  | F |
| ilimit | Current limit |  | A |
| Current Control |  |  |  |
| τscr | Synchronous current regulator time constant |  | second |
| τscroff | SCR turn off time constant |  | second |
| ifcl | Integral feedback current limit |  | A |
| Hybrid or Sampled Delta Modulator |  |  |  |
| fsmple | Per phase sampling frequency |  | Hz |
| h | Hysteresis level |  | A |

| Internal Variable Name | Description | Units |
| --- | --- | --- |
| Ossim | Operate inverter module (true to operate) | logical |
| iin | DC current into bridge converter | A |
| Sa | a-phase switching signal (true is upper on) | logical |
| Sb | b-phase switching signal (true is upper on) | logical |
| Sc | c-phase switching signal (true is upper on) | logical |
| iaL | a-phase inductor current (out of inverter) | A |
| ibL | b-phase inductor current (out of inverter) | A |
| icL | c-phase inductor current (out of inverter) | A |
| vaR | a-phase inverter line-to-bottom rail voltage | V |
| vbR | b-phase inverter line-to-bottom rail voltage | V |
| vcR | c-phase inverter line-to-bottom rail voltage | V |
| vabO | measured a- to b-phase voltage | A |
| vbcO | measured b- to c-phase voltage | A |
| iaL | measured a-phase inductor current (into inverter) | A |
| ibL | measured b-phase inductor current (into inverter) | A |
| iaO | measured a-phase output current | A |
| ibO | measured b-phase output current | A |
| mssim | nonlinear stabilizing control modulation signal |  |
| iaL | a-phase inductor current command | A |
| ibL | b-phase inductor current command | A |
| icL | c-phase inductor current command | A |
| qe | Synchronous reference frame position | rad |

# Macro format

MACRO SSIM(z,on,off,vdc,iaO,ibO,vthev,rthev,vabO,vbcO,vcaO, &

par_vqestar,par_westar, &

par_cin,par_rcin,par_vsw,par_rsw,par_vd,par_rd, &

par_lac,par_rl,par_cac,par_rc, &

par_vinmin1,par_vinmax1, &

par_vinmin2,par_vinmax2,par_tausupc, &

par_gainvab,par_offsetvab,par_gainvbc,par_offsetvbc, &

par_gainiaO,par_offsetiaO,par_gainibO,par_offsetibO, &

par_gainiaL,par_offsetiaL,par_gainibL,par_offsetibL, &

par_kpvc,par_kivc,par_ceq,par_ilimit, &

par_tauscr,par_tauscroff,par_ifcl, &

par_fsmple,par_h)

# Validation

These models have been validated via hardware experimentations.

NLAM_SSIM : NLAM of an inverter module

Author: S. D. Sudhoff

Author contact: sudhoff@purdue.edu,

Date:

Macro name: SSIM

Version number:  NCS 3.1

Report errors or changes to: sudhoff@purdue.edu

# Brief Description

NLAM Model of a Ship Service Inverter Module.

# List of Inputs, Outputs, Parameters, and Internal variable

| Variable Name | Description | Units |
| --- | --- | --- |
| z | Concatenation variable |  |

| Input Variable Name | Description | Units |
| --- | --- | --- |
| on | Logical command to turn on converter | logical |
| off | Logical command to turn off converter | logical |
| vdc | Inverter module DC input voltage | V |
| iqO | q-axis current out of the inverter module | A |
| idO | d-axis current out of the inverter module | A |

| Output Variable Name | Description | Units |
| --- | --- | --- |
| vthev | Instantaneous Thevinen equivalent input voltage | V |
| rthev | Instantaneous Thevinen equivalent input resistance |  |
| vqO | q-axis output voltage (line-to-reference) | V |
| vdO | d-axis output voltage (line-to-reference) | V |
| ωe | radian frequency of output | rad/S |

| Parameter Name | Description | Default Value | Units |
| --- | --- | --- | --- |
| Set Up |  |  |  |
| vqe∗ | q-axis voltage command |  | V |
| ωe | Command output frequency |  | rad/s |
| Bridge |  |  |  |
| Cin | Input capacitance |  | F |
| rCin | Input capacitor effective series resistance |  |  |
| vsw | Switch nominal forward voltage drop |  | V |
| rsw | Switch forward resistance |  |  |
| vd | diode nominal forward voltage drop |  | V |
| rd | diode forward resistance |  |  |
| LC Filter |  |  |  |
| Lac | Inductance of AC filter |  | H |
| rL | Series resistance of inductor |  |  |
| Cac | Capacitor in delta-connection |  | F |
| rC | Series resistance of capacitor |  |  |
| Supervisory Control |  |  |  |
| vinmin1 | Lowest input voltage to start converter |  | V |
| vinmax1 | Highest input voltage to start converter |  | V |
| vinmin2 | Lowest input voltage to keep running |  | V |
| vinmax2 | Highest input voltage to keep running |  | V |
| τsc | Time constant of supervisory control |  | second |
| Sensors |  |  |  |
| Voltage Control |  |  |  |
| Kpv | Voltage control proportional gain |  | A/V |
| Kiv | Voltage control integral gain |  | A/Vs |
| Ceq | estimated equivalent line-neutral capacitance |  | F |
| ilimit | Current limit |  | A |
| Current Control |  |  |  |
| τscr | Synchronous current regulator time constant |  | second |
| τscroff | SCR turn off time constant |  | second |
| ifcl | Integral feedback current limit |  | A |
| Hybrid or Sampled Delta Modulator |  |  |  |
| kcmeff | Effective gain of delta modulator |  | V/A |

| Internal Variable Name | Description | Units |
| --- | --- | --- |
| Ossim | Operate inverter module (true to operate) | logical |
| iin | DC current into bridge converter | A |
| iqL | q-axis inductor current (out of inverter) | A |
| idL | d-axis inductor current (out of inverter) | A |
| vqR | q-axis inverter line-to-bottom rail voltage | V |
| vdR | d-axis inverter line-to-bottom rail voltage | V |
| iqL | q-axis inductor current command | A |
| idL | d-axis inductor current command | A |
| mq | q-axis modulation command |  |
| md | d-axis modulation command |  |

# Macro format

MACRO NLAM_SSIM(z, on,off,vdc,iqO,idO, vthev,rthev,&

vqO,vdO,we, &

par_vqestar,par_westar, &

par_cin,par_rcin,par_vsw,par_rsw,par_vd,par_rd, &

par_lac,par_rl,par_cac,par_rc, &

par_vinmin1,par_vinmax1, &

par_vinmin2,par_vinmax2,par_tausupc, &

par_kpvc,par_kivc,par_ceq,par_ilimit, &

par_tauscr,par_tauscroff,par_ifcl, &

par_kcmeff)

# Assumptions in Model Derivation

# All variables are represented in the synchronous reference frame unless otherwise noted.

# Validation

These models have been validated via hardware experimentations.