# Synchronous machine/Excitation system

Macro file name: sm_exciter.mac

Macro name:  PEAKCALC_SM_EXCITER,SSC_SM_EXCITER,VRCONT_SM_EXCITER,

SHC_SM_EXCITER, EXCITER_MACHINE,SM_EXCITER

Version number: NCS 3.1

The synchronous machine and excitation system is illustrated in Figure 1.  In this system, the voltage regulator has two parts; a control algorithm to determine the field current of the brushless exciter, and a power converter which achieves this command.  The brushless exciter machine rotor voltage is rectified – which in turn supplies the field current to the synchronous machine. Principal variables include the commanded rms line-to-line , the brushless exciter field voltage and current  and , the synchronous machine field voltage and current  and , the synchronous machine line-to-line voltages  and , and the a- and b- phase currents into the synchronous machine and .

Figure 1 : Synchronous machine/exciter.

The operation of the excitation system begins with the peak detector, which computes the peak value of the fundamental component of both the voltage and current waveforms.  This control is depicted in Figure 2.  Therein, and throughout this work, variables of the form  and  denote measured and estimated values of , where  is an arbitrary variable.  In Figure 2, the inputs are the measured line-to-line voltages and two of the phase currents and the two line currents.  The remaining control input is, the position of a synchronous reference frame. Based on these quantities, estimate values for the peak of the line-to-neutral voltage and peak line current, and are determined.  The high and low pass filters shown in Figure 2 are of the form

(1)

and

(2)

wheres, andms. The transformations for line-to-line voltage and  for line currents to qd voltages and currents, respectively are given by

(3)

and

,	(4)

respectively.

Figure 2:  Block diagram of the peak detector.

Based upon the output of the peak detector, the exciter supervisory control depicted in Figure 3 is used to determine the operating status of the voltage control.  To this end, logical flags and are created to verify that the voltage and current peaks are acceptable; these flags are then used in accordance with the state transition diagram to determine the operating status (high to operate voltage regulator).  In Figure 3,  ON and OFF are logical inputs to request turn on and turn off of the control respectively.

Figure 3: Exciter supervisory control.

Based on the voltage command, peak detector, and operating status, the regulatory control depicted in Figure 4 is used to determine a current command to the brushless exciter field current .The power stage of the voltage regulator is depicted in Figure 5. The transformer parameters are such that when rated ac voltage and frequency are applied to the transformer primary, the rectifier (excluding the capacitor) may be represented as a voltage of 25 V in series with a resistance of 1.4 , an inductance of 6 mH, and an ideal diode.  The switching of the power semiconductors is in accordance with a hysteresis current regulator with a band of 18 mA (center to peak).

Figure 4: Exciter regulation control

Figure 5: Power stage of voltage regulator.

The brushless exciter itself is an 8-pole synchronous machine.  Perhaps the most difficult part of modeling this machine is the high degree of magnetic hysteresis present.  Nevertheless, the equivalent circuit shown in Figure 6 has been found to adequately portray machine dynamics.

The primary synchronous machine is a 4-pole device. It is modeled using the equivalent circuit depicted in Figure 7.  Therein, the magnetizing flux linkages are related to the magnetizing fluxes by  and  where

Lmd=0.02397+0.03615λ2−0.01669λ41+0.99384λ2−0.022485λ4	(5)

Lmd=0.01257+0.01895λ2−0.00875λ41+1.0892λ2−0.3123λ4	(6)

and where

(7)

For the test machine .

The damper winding and field winding transfer functions may be expressed

(8)

(9)

(10)

Figure 6: Equivalent circuit of exciter machine.

Figure 7: Equivalent circuit of primary generator.

SM_EXCITER : Brushless exciter model

Author: S. D. Sudhoff

Author contact: sudhoff@purdue.edu,

Date:

Macro name: SM_EXCITER

Version number:  NCS 3.1

Report errors or changes to: sudhoff@purdue.edu

# Brief Description

Brushless exciter model.

# List of Inputs, Outputs, Parameters, and Internal variable

| Variable Name | Description | Units |
| --- | --- | --- |
| z | Concatenation variable |  |

| Input Variable Name | Description | Units |
| --- | --- | --- |
| ifdsm | current out of exciter into synchronous machine field | A |
| ωrm | exciter mechanical rotational speed | rad/s |
| qrm | exciter mechanical angle | A |
| vqsm | q-axis synchronous machine terminal voltage | V |
| vdsm | d-axis synchronous machine terminal voltage | V |
| iqsm | q-axis current into synchronous machine | A |
| idsm | d-axis current into synchronous machine | A |
| vllrms | commanded line-to-line voltage | V |
| on | logical command to turn on converter | logical |
| off | logical command to turn off converter | logical |

| Output Variable Name | Description | Units |
| --- | --- | --- |
| vfdsm | voltage out of exciter into SM. field | V |
| Te | electromagnetic torque of exciter machine | Nm |
| vfde | stationary dc field voltage of exciter | V |
| ifde | stationary dc field current of exciter | V |

| Parameter Name | Description | Default Value | Units |
| --- | --- | --- | --- |
| Sensors |  |  |  |
| gainVab | gain of sensor measuring vab |  |  |
| offsetVab | offset of sensor measuring vab |  | V |
| gainVbc | gain of sensor measuring vbc |  |  |
| offsetVbc | offset of sensor measuring vbc |  | V |
| gainia | gain of sensor measuring ia |  |  |
| offsetia | offset of sensor measuring ia |  | A |
| gainib | gain of sensor measuring ib |  |  |
| offsetib | offset of b-phase output current sensor |  | A |
| gainifde | gain of sensor measuring ifde |  |  |
| offsetifde | offset of sensor measuring ifde |  | A |
| Setting reference frame |  |  |  |
| Psm | number of electrical poles on synchronous machine |  |  |
| qrsm0 | synchronous machine position at t=0 |  | rad |
| Peak detector (PEAKCALC_SM_EXCITER) |  |  |  |
| τ0 | HPF time constant |  | sec. |
| τf | LPF time constant |  | sec. |
| Supervisory Control Controller (SSC_SM_EXCITER) |  |  |  |
| vllmax | maximum allowable line-to-line voltage |  | V (rms) |
| ipkmax | maximum allowable peak line current |  | A |
| Voltage Regulating Controller (VRCONT_SM_EXCITER) |  |  |  |
| τvr | Integral part time constant |  | sec |
| kpv | Proportional part gain |  | A/V |
| ifdemax | Maximum exciter field current command |  | A |
| Simple Hysteresis Controller (SSC_SM_EXCITER) |  |  |  |
| ΔI | Hysteresis Bandwidth (from -DeltaI to +DeltaI) |  |  |
| vdcpow | dc voltage of the power supply |  | V |
| rswitch | total series resistance of switch |  |  |
| vswitch | total series voltage drop of switch |  | V |
| rdiode | total series resistance of diode |  |  |
| vdiode | total series voltage drop diode |  | V |
| rseries | resistance in series with power supply |  |  |
| Lseries | inductance in series with power supply |  | H |
| Cdc | dc capacitance of power supply |  | F |
| Exciter Machine |  |  |  |
| P | Number of poles on exciter machine |  |  |
| λpm | permanent magnet flux linkage |  | Vs |
| Lfd | field leakage inductance (ref. to rotor) |  | H |
| rfd | field winding resistance (ohm, ref. to rotor) |  |  |
| rr | rotor winding resistance |  |  |
| Lmd | d-axis magnetizing inductance |  | H |
| Ldd | d-axis damper winding inductance |  | H |
| rdd | d-axis damper winding resistance |  |  |
| Lmq | q-axis magnetizing inductance |  | H |
| Ldq | q-axis damper winding inductance |  | H |
| rdq | q-axis damper winding resistance |  |  |
| N | Equivalent turns ratio |  | Nr/Nf |
| qr0 | initial electrical rotor angle |  | rad |
| 3-Phase Rectifier |  |  |  |
| rlo | rectifier resistance in on state |  |  |
| rhi | rectifier resistance in on off state |  |  |

| Internal Variable Name | Description | Units |
| --- | --- | --- |
| vasm | synchronous machine a-phase voltage | V |
| vbsm | synchronous machine b-phase voltage | V |
| vcsm | synchronous machine c-phase voltage | V |
| iasm | synchronous machine a-phase voltage | A |
| ibsm | synchronous machine b-phase voltage | A |
| icsm | synchronous machine c-phase voltage | A |
| vabsmmeas | measured voltage between phases ab of the SM | V |
| vbcsmmeas | measured voltage between phases bc of the SM | V |
| iasmmeas | measured input current of phase a of the SM | A |
| ibsmmeas | measured input current of phase b of the SM | A |
| ifdemeas | measured exciter stationary current | A |
| qe | electric position of generator synch. ref frame | A |
| vlnpk | peak value of line-to-neutral voltage | V |
| ipk | peak value of line current | A |
| op | operating status of exciter | logical |
| ifde | commanded exciter field current | A |
| iar | a-phase exciter machine current | A |
| ibr | b-phase exciter machine current | A |
| icr | c-phase exciter machine current | A |
| valr | a-phase voltage to lower rail out of rectifier | V |
| vblr | b-phase voltage to lower rail out of rectifier | V |
| vclr | c-phase voltage to lower rail out of rectifier | V |
| var | a-phase exciter machine voltage | V |
| vbr | b-phase exciter machine voltage | V |
| vcr | c-phase exciter machine voltage | V |

# Macro format

MACRO SM_EXCITER(z, ifdsm,wrm,qrm,vqsm,vdsm,iqsm,idsm,vllrmsstar,on,off, &

vfdsm,te,vfde,ifde, &

par_gainvab,par_offsetvab, &

par_gainvbc,par_offsetvbc, &

par_gainia,par_offsetia, &

par_gainib,par_offsetib, &

par_gainifde,par_offsetifde, &

par_Psm,par_qrsm0, &

par_tauzero,par_tauf, &

par_vllmax,par_ipkmax, &

par_tauvr,par_kpv,par_ifdemax, &

par_DeltaI,par_vdcpow, &

par_rswitch,par_vswitch, &

par_rdiode,par_vdiode, &

par_rseries,par_Lseries,par_Cdc, &

par_P,par_lampm, &

par_Llfd,par_rfd,par_rr, &

par_Lmd,par_Ldd,par_rdd, &

par_Lmq,par_Ldq,par_rdq, &

par_N,par_qr0, &

par_rlo,par_rhi)

# Validation

These models have been validated via hardware experimentations.