# Component Heat Exchanger

Author: Y. Lee, E. L. Zivi and A. M. Cramer

Author contact: ylee@usna.edu, zivi@usna.edu

Date: 9 / 22/ 2006

Model name: ComponentHeatExchanger.mac

Version number: IRIS 1.0

Report errors or changes to: ylee@usna.edu

# Brief Description

Power component heat dissipation is removed through conduction from the power components to a “cold plate” heat sink. This cold plate is then cooled via convective heat transfer to a cooling fluid as illustrated in the figure 1. Typically the cooling fluid is saltwater (seawater), freshwater, or chilled water.

Fig 1.  Cold plate heat exchanger

# Validity Range and Limitations

N/A

# List of Inputs, Outputs, Parameters, and Internal variable

| Variable Name | Description | Units |
| --- | --- | --- |
| z | Concatenation variable |  |

| Input Variable Name | Description | Units |
| --- | --- | --- |
|  | Heat transfer rate from the component | W |
|  | Mass flow rate of the cooling fluid | kg/s |
|  | Temperature of the incoming flukd | K |

| Output Variable Name | Description | Units |
| --- | --- | --- |
|  | Temperature of the outgoing fluid | K |
|  | Temperature of the cold plate | K |

| Parameter Name | Description | Default Value | Units |
| --- | --- | --- | --- |
|  | Mass of the cold plate |  | Kg |
|  | Specific heat of the cold plate |  | J/kg/K |
|  | Specific heat of the cooling fluid |  | J/kg/K |
| A | Cooling fluid contact area |  | m2 |
| h | Cooling fluid heat transfer coefficient | 4800 | W/ m2/K |

| Internal Variable Name | Description | Units |
| --- | --- | --- |
|  | Heat transfer rate from the cold plate to fluid | W |
| p | Time derivative of the temperature of the cold plate | K/s |

# Macro format

MACRO ComponentHeatExchanger(z,qin,wcf,tci,&

tco,thx,&

par_mhx,par_chx,par_ccf,par_A,par_h)

# Assumptions in Model Derivation

The power component heat dissipation is determined from the power component efficiency

(1)

Heat source parameter

power component efficiency (dimensionless)

Heat source input

component power (W)

Heat source output

heat flow from the power component (W = J/s)

Note that this formulation for  is independent of the cold plate temperature and the thermal resistance between the power components and the cold plate. These assumptions are consistent with the customary deactivation of power components from excessive cold plate temperature.

The heat exchanger is assumed to be well insulated and the fluid flow is assumed to be one dimensional “plug” flow.

# Mathematical Description

The net heat flow into the heat exchanger cold plate is the difference between the heat flow from the power components and the heat flow removed by the cooling fluid. This net heat flow determines the cold plate rate of temperature change

pThx=Qin−Qhxmhxchx	(2)

The heat flow from the cold plate to the cooling fluid is governed by the convective heat transfer from the cold plate to the cooling fluid

Qhx=Ah(Thx−Tca)	(3)

where Tca is the average fluid temperature.

From conservation of energy, the heat flow removed by the cooling fluid can be specified in terms of flow rate, specific heat and fluid heating as

.	(4)

Neglecting transient fluid thermodynamics along the interior of the heat exchanger produces a lumped parameter fluid model wherein  and the average fluid temperature is

(5)

Substituting (5) into (3) provides the cold plate to cooling fluid heat transfer rate in terms of inlet and outlet fluid temperatures

Qhx=AhThx−Tci+T2	(6)

Rearranging (6) yields the outlet temperature of the cooling fluid as

Tco=2Thx−QhxAh−Tci	(7)

Using the  approximation, (4) can be rearranged so that

.	(8)

Substituting (8) into (6) yields the heat transfer rate in terms of the cold plate temperature, inlet cooling fluid temperature and flow rate

Qhx=2wcfccfAh2wcfccf+AhThx−Tci	(9)

However, this formulation is only valid if the cooling fluid flow rate is sufficient so that the heat transfer rate to the fluid, , does not exceed the cooling fluid heat removal capacity defined by constraining (4) to . If the cooling fluid heat removal capacity is saturated, then  and from (4)

.	(10)

Comparing (6) and (9) at the  boundary condition provides a convenient test to ensure that the heat transfer to the fluid does not exceed the heat removal capacity of the fluid

2wcfccf≥Ah.	(11)

In summary, (2),(7),(9), (10) and (11) provide the final cold plate heat exchanger thermal model including thermal saturation.

pThx=Qin−Qhxmhxchx where   if 2wcfccf≥Ah then Qhx=2wcfccfAh2wcfccf+AhThx−Tci

and

else    and